## Slide 1: Time of Use and Demand Metering -
WHY THEY ARE IMPORTANT
July 24, 2024
8:45 AM -- 10:15 AM
Carl Chermak

## Slide 2: Electric Power and Energy
Power (P)
Rate at which energy is produced or consumed
Measured in Watts or kW*
At any single point in time, P = V x I
Energy (W, for Work)
Summation of power applied over time
Measured in Watthours or kWh*

## Slide 3: Electric Power and Energy
Power is like your car’s rate of speed as shown on the speedometer.
Energy is like your car’s traveled distance as shown on the odometer.
80972

## Slide 4: Measuring What is Delivered
Gallons
Gallons/Hr
Watt-hours
Watts
Cubic feet/Hr
Cubic feet
Gallons
Gallons/Hr

## Slide 5: Principles of Demand Metering
The average value of power (or related quantity) over a specified period of time
  Expressed in units of:
    kilowatts (kW)
    kilovolt-amperes (kVA)
    kilovars (kvar)
    amperes (A)
  Or other suitable units
What is “Demand”?

## Slide 6
WHY IS DEMAND IMPORTANT?
Heavier loads tax the utility system more than smaller loads, and require larger equipment for generation, transmission, and distribution
Utilities must recover for the costs of the infrastructure necessary to support the larger loads
Demand is a measure of the impact of a consumer’s loads
Demand is used to determine how much a consumer should share in paying for infrastructure

## Slide 7
WHY IS DEMAND IMPORTANT?
More equitably allocates the “cost of service” to users
Provides information on unexpected customer load growth
kW demand is relatively easy to measure and record

## Slide 8: Demand and Cost Recovery
Utilities meter for Energy Consumption (kWh) in order to recover for cost of fuel.
For larger, typically C&I customers, utilities also meter for Peak Demand in order to recover for cost of infrastructure.

## Slide 9
VOCABULARY
Power: The rate at which energy is being used (watts)
Energy: The total use of power over a period over time (watt hours)
Demand: The average value of power (or related quantity) over a specified period of time.
Demand Interval: The length of the interval of time upon which the demand measurement is based.
Block Demand: Demand calculation based on a single demand interval.
Rolling Demand: Demand calculation based on several demand sub-intervals.

## Slide 10
VOCABULARY (Con’t)
Maximum Demand: The largest of a particular type of demand occurring within a specified period, such as one month. Also called peak demand.
Cumulative Demand: The sum of the previous billing period maximum demand readings. At time of billing period reset, the maximum demand for the most recent billing period is added to the previously accumulated total of all maximum demands.
Continuously Cumulative Demand: The sum of the previous billing period maximum demands (cumulative demand), and the present period maximum demand.

## Slide 11
Demand is the average power calculated for every demand interval, simply Energy / Time.
Example: For 10 kWh consumed in a 15-minute demand interval,
Demand = 10 kWh / 0.25 h
Demand = 40 kW
A watthour-demand meter keeps a record of the Peak Demand since the last demand reset, and this is used for billing.
HOW DO WE MEASURE FOR DEMAND?

## Slide 12
15 min
15 min
15 min
15 min
200 kW
100 kW
300 kW
Energy: 48 kWh 46 kWh 47 kWh 50 kWh
Demand: 192 kW 184 kW 188 kW 200 kW
(peak)
demand reset
BLOCK DEMAND
Energy is equal to the area under this power curve
Instantaneous Power
Demand
Demand
Demand
Demand

## Slide 13
200 kW
100 kW
300 kW
ROLLING DEMAND
5
min
5
min
5
min
5
min
5
min
5
min
5
min
5
min
5
min
5
min
5
min
5
min
192 kW
184 kW
215 kW
188 kW
145 kW
223 kW
208 kW
150kW
238 kW
(peak)
Instantaneous Power
demand reset
200 kW

## Slide 14: Peak and Cumulative Demand

## Slide 15: What is Load Profile?
Load Profile Data is a collection of discrete time interval metering data (kWh, kVAh, V2h, etc.) recorded for each channel in a meter over a user-defined period of time. Load Profile parameters have to be defined for every account. The parameters in specific may be:
Interval size in time units*
Interval length, i.e. number of such intervals*
Channel unit of measurement*
TOU (time-of-use) Calendar name
TOU Schedule name

## Slide 16: Time of Use (TOU)
Large utilities generate power from a variety of sources
Fuel costs are very low for some types of plants, higher for others
Very large and efficient “base-load” plants (the newest coal or nuclear plants) may have very low fuel cost. These also run 24 hours per day and every day possible
Some old or less efficient plants are run only when the need is great, perhaps for only a few hours each day
Some plants with very high fuel cost may be run only in emergencies

## Slide 17
Time of Use (TOU)
The result: Varying energy cost as overall demand varies according to hour, type of day, and season
So, a utility may offer lower pricing during “off-peak” periods when the energy is less costly, and impose higher pricing during “on-peak” periods when more costly plants must be run.
This is known as TOU Billing.

## Slide 18
1. TOU Billing more fairly allocates for the varying energy costs.
2. Consumers are incentivized to reschedule their loads. Utilities often assist consumers with tools to predict billing outcomes.
The resulting schedule changes can drive an overall flatter load curve, decreasing the dependence on the higher cost power plants.
OK, so how do we meter for that?
Time of Use (TOU)

## Slide 19: Time of Use Metering
  A TOU meter accumulates energy, calculates demand and registers the data into specific rate “buckets” depending on the time of day
  TOU rate periods are typically called Peak, Shoulder Peak, Off Peak
  Different days of the week and holidays may have different TOU rate schedules
  You can have different “Seasons”
  TOU metering requires the meter to keep time and programmable dates are stored in calendars
  Meter can be programmed for self reads or demand resets on specific dates

## Slide 20: T-76 Register
What did a TOU meter look like back in the day?

## Slide 21: TOU and Demand Metering
Thank you
Carl Chermak
315-436-8696