## Slide 1: ANSI Meter Forms
Prepared by Perry Lawton, TESCO
The Eastern Specialty Company
For North Carolina Electric Meter School
Polyphase Track
Monday June 10, 2024
2:45 PM

## Slide 2: Agenda
Meters 101 - Electro-Mechanical vs Solid-State
Meter Forms
Self-Contained vs Transformer Rated
Blondel’s Theorem
Available References (Hardy’s Power Measurement Handbook, UGLY’s Elect Ref)
Examples
1S, 2S, 3S, 4S, 5/35S, 8/9S, 16S

## Slide 3: Induction Meters
Two coils and a conducting (usually aluminum) disk. A braking magnet.
Magnetic field from the first coil generates eddy currents in the disk
Magnetic field from the second coil interacts with the eddy currents to cause motion
Disk would accelerate without bound except for eddy currents caused by motion through fixed magnetic field which slows the disk
The end result is that each revolution of the disk measures a constant amount of energy

## Slide 4: Basic Energy Formula
The essential specification of a watthour meter’s measurement is given by the value Kh [ Watthours per disk revolution ]
A Kh of 7.2 is typical. In this example, each full rotation of the disk is equivalent to 7.2Wh of energy.
The watthour meter formula is as follows:
tescometering.com
4

## Slide 5: Meters 101 – Solid-State
CURRENT TRANSFORMER
POTENTIAL TRANSFORMER
ADC
FILTER
ADC
FILTER
MICRO
PROC
DISPLAY
COMM
PULSE
Overview of Functionality
Potential and Current is scaled down and conditioned with transformers and filters
ADC’s (analog to digital converters) digitize the signals
A micro-processor or DSP executes the calculations
Resulting data is displayed, sent externally via the communication circuits, and used for the calibrated pulse output

## Slide 6: Meter Forms
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S

## Slide 7: Meter Forms

## Slide 8: Meter Forms
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S

## Slide 9: Meter Forms
TRANSFORMER-RATED
1S
2S
3S
4S
5S
6S
9S
12S
15S
16S
25S
45S
10S
11S
13S
14S
17S
24S
32S
39S
26S
35S
46S
56S
66S
76S
7S
8S
29S
36S
SELF-CONTAINED

## Slide 10: Self-Contained Meters
Relatively Low Current
Example: 100A
Primarily Residential

## Slide 11: Self-Contained
Primarily Residential

## Slide 12: Transformer-Rated Meters
Relatively High Current
Example: 4000A
Primarily Commercial/Industrial
Notes: 12

## Slide 13: Transformer-Rated Meters
Primarily Commercial/Industrial

## Slide 14: Diagram Example
References
Power Measurements Handbook, Dr. Bill Hardy
UGLY’s Electrical References
Meterman’s Handbook
Manufacturer’s websites

## Slide 15: Diagram Example
References
Power Measurements Handbook, Dr. Bill Hardy
UGLY’s Electrical References
Meterman’s Handbook
Manufacturer’s websites

## Slide 16: Diagram Example
3 Current Coils
3 Potential Coils

## Slide 17: Blondel’s Theorem
French Electrical Engineer Andre Blondel
Attempt to simplify electrical measurements and validation of the results
Paper submitted to the International Electric Congress in Chicago in 1893.
E = n - 1
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.

## Slide 18: Blondel’s Theorem
E = n - 1
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.
1S
12S
9S
Blondel Compliant

## Slide 19: Blondel’s Theorem
E = n - 1
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.
2S
Non-Blondel Compliant

## Slide 20: Blondel’s Theorem
Why is non-Blondel metering bad?
Makes assumptions about the service
Example: balanced voltages
Assumptions might not be true
When these assumptions are not true, then there are power measurement errors even if the meter is working perfectly.
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.

## Slide 21: Blondel’s Theorem
Why are non-Blondel meters used?
Fewer elements (meters) = lower cost
Especially true for electro-mechanical meters
Fewer CT’s and PT’s = lower cost
Less wiring and cheaper sockets
The theorem states that the power provided to a system of N conductors is equal to the algebraic sum of the power measured by N watt-meters. The N watt-meters are separately connected such that each one measures the current level in one of the N conductors and the potential level between that conductor and a common point. In a further simplification, if that common point is located on one of the conductors, that conductor's meter can be removed and only N-1 meters are required.

## Slide 22: Metering Examples

## Slide 23: Metering Examples

## Slide 24: Metering Examples

## Slide 25: Metering Examples

## Slide 26: Metering Examples

## Slide 27: References
Wikipedia – of course
https://en.wikipedia.org/wiki/Blondel%27s_theorem
Power Measurement Handbook – Dr. Bill Hardy – TESCO CTO Emeritus
http://www.powermeasurements.org/library/Presentations/NCMS%202013%20-%20Non-Blondel%20Metering.pdf
Third Party meter sites
https://www.baycitymetering.com/

## Slide 28: Agenda
Meters 101 - Electro-Mechanical vs Solid-State
Meter Forms
Self-Contained vs Transformer Rated
Blondel’s Theorem
Available References

## Slide 29: Questions and Discussion
Perry Lawton
Northeastern Regional Sales Manager
perry.lawton@tescometering.com
TESCO Metering Bristol, PA
215.500.7511
This presentation can also be found under Meter Conferences and Schools on the TESCO website: tescometering.com
ISO 9001:2015 Certified Quality Company
ISO 17025:2017 Accredited Laboratory

## Slide 30: Tesco hospitality suite
We would like you to join us in the TESCO Hospitality Suite for networking and more discussions about metering. The discussion will not be exclusively metering……….but we love metering and that is the most common topic.
TESCO Hospitality Suite – Brighton Tower
Monday and Tuesday 8:00 PM – 10:00 PM